## Data Entry Sheet
ANSI C119.1
Current Cycle Data Sheet
Class of Test |  | A
Test Method: |  | CCT | Select Test Method
Connector Type: |  | Mechanical |  | Select Connector Type
Part Tested: |  | xxxxxx
Date Started: |  | 2009-01-26
Date Completed:_ |  | 2009-03-10
Project # |  | 12345
Current Cycle: On Period (Hrs) |  |  | 1
Off Period (Hrs) |  |  | 1
Test Current: |  |  | 225 | Amps
Cable (main) |  |  | Cable (Tap)
Size | 1/0 |  | Size |  |  |  | Conductor Preparation: | Compounded? |  | YES
Type | AL |  | Type |  |  |  |  | Compound |  | xx
Stranding | 19 |  | Stranding |  |  |  |  | Wire Brushed? |  | Yes
Insulation | USE |  | Insulation
Length | 12 |  | Length
Number of screws(bolts) per conductor |  |  |  | 1
Screw (bolt) size |  | 7/16
Torque (in-lb) |  | 120
* Record Ambient at time resistance is measured
Measurement Point | Req'd Cycle Number | Actual Cycle number | Connector Temp (°C) |  |  |  | Control Conductor (°C) | Ambient (°C) | Cycle Number | Connector Resistance (Measured)
[10 empty] | Ambient @ Reading (°C) | Micro Ohms (μΩ)
|  |  | C1 | C2 | C3 | C4 |  |  |  |  | C1 | C2 | C3 | C4
1 | 25-30 | 25 | 101 | 105 | 106 | 106 | 123 | 24 | 25 | 24 | 386.1 | 391.6 | 400 | 407.4
2 | 45-55 | 50 | 102 | 107 | 108 | 108 | 124 | 24 | 50 | 24 | 386.8 | 392.1 | 400.4 | 408.4
3 | 70-80 | 75 | 101 | 106 | 111 | 111 | 125 | 23 | 75 | 23 | 387.4 | 392 | 400.5 | 409.2
4 | 95-105 | 100 | 100 | 105 | 111 | 109 | 128 | 24 | 100 | 24 | 387.6 | 392 | 401.2 | 409.6
5 | 120-130 | 125 | 101 | 105 | 106 | 107 | 122 | 22 | 125 | 22 | 384 | 389.4 | 398.6 | 406.2
6 | 160-170 | 165 | 103 | 105 | 109 | 112 | 124 | 22 | 165 | 22 | 386.1 | 391.7 | 400.2 | 408.5
7 | 200-210 | 204 | 101 | 105 | 106 | 108 | 124 | 25 | 204 | 25 | 388.6 | 394.4 | 404.7 | 411.9
8 | 245-255 | 251 | 101 | 104 | 109 | 110 | 124 | 24 | 251 | 24 | 389.9 | 395.8 | 405.9 | 412
9 | 320-330 | 329 | 105 | 109 | 113 | 114 | 128 | 24 | 329 | 24 | 392.1 | 397.5 | 407.3 | 414.5
10 | 400-410 | 406 | 103 | 106 | 108 | 108 | 125 | 25 | 406 | 25 | 389 | 394.4 | 404.5 | 411.5
11 | 495-505 | 496 | 105 | 109 | 110 | 110 | 127 | 23 | 496 | 23 | 388.3 | 394 | 403.3 | 410.2
Note on J34: rwestbrook: Added Color and numbers here Our lab techs asked for this to be able to follow straight across from the measurement point
Note on E19: rwestbrook: Type in AL, CU, ACSR
Note on C6: Select Mechanical or Compression
Note on B37: XP: Type in Actual Cycle #

## Stability
ANSI C119.1
Current Cycle Report Data Sheet
Class of Test |  | A | [9 empty] | Test Method: |  | CCT
Part Tested: |  | xxxxxx |  | Date Started: |  | 2009-01-26 |  | Date Completed:_ |  | 2009-03-10 |  | Project # | 12345
Cable (main) | Size | 1/0 | Cable (Tap) | Size |  |  |  | Conductor Preparation: | Compounded? |  | YES
| Type | AL |  | Type |  |  |  |  | Compound |  | xx
| Stranding | 19 |  | Stranding |  |  |  |  | Wire Brushed? |  | Yes
| Insulation | USE |  | Insulation
| Length | 12 |  | Length
Current Cycle: On Period (Hrs) |  |  | 1 | Off Period (Hrs) |  | 1 |  | Test Current: |  | 225 | Amps
Connector Type: | Mechanical
Number of screws(bolts) per conductor |  |  | 1 |  | Screw (bolt) size |  | 7/16 | Torque (in-lb) |  | 120
Screw (bolt) size
Measurement Points | Cycle Number | Ambient (°C) | Control Conductor (°C) | Connector Temp (°C) |  |  |  | Temperature Difference (°C) |  |  |  | Stability Factor (Si)
|  |  |  | C1 | C2 | C3 | C4 | C1 | C2 | C3 | C4 | C1 | C2 | C3 | C4
1 | 25 | 24 | 123 | 101 | 105 | 106 | 106 | 22 | 18 | 17 | 17 | 0.81818 | 0.90909 | 0.90909 | 1.4545
2 | 50 | 24 | 124 | 102 | 107 | 108 | 108 | 22 | 17 | 16 | 16 | 0.81818 | 1.9091 | 0.090909 | 0.45455
3 | 75 | 23 | 125 | 101 | 106 | 111 | 111 | 24 | 19 | 14 | 14 | 1.1818 | 0.090909 | 2.0909 | 1.5455
4 | 100 | 24 | 128 | 100 | 105 | 111 | 109 | 28 | 23 | 17 | 19 | 5.1818 | 4.0909 | 0.90909 | 3.4545
5 | 125 | 22 | 122 | 101 | 105 | 106 | 107 | 21 | 17 | 16 | 15 | 1.8182 | 1.9091 | 0.090909 | 0.54545
6 | 165 | 22 | 124 | 103 | 105 | 109 | 112 | 21 | 19 | 15 | 12 | 1.8182 | 0.090909 | 1.0909 | 3.5455
7 | 204 | 25 | 124 | 101 | 105 | 106 | 108 | 23 | 19 | 18 | 16 | 0.18182 | 0.090909 | 1.9091 | 0.45455
8 | 251 | 24 | 124 | 101 | 104 | 109 | 110 | 23 | 20 | 15 | 14 | 0.18182 | 1.0909 | 1.0909 | 1.5455
9 | 329 | 24 | 128 | 105 | 109 | 113 | 114 | 23 | 19 | 15 | 14 | 0.18182 | 0.090909 | 1.0909 | 1.5455
10 | 406 | 25 | 125 | 103 | 106 | 108 | 108 | 22 | 19 | 17 | 17 | 0.81818 | 0.090909 | 0.90909 | 1.4545
11 | 496 | 23 | 127 | 105 | 109 | 110 | 110 | 22 | 18 | 17 | 17 | 0.81818 | 0.90909 | 0.90909 | 1.4545
|  |  |  | Average Temperature Difference |  |  |  | 22.8182 | 18.9091 | 16.0909 | 15.5455
|  |  |  | Maximum Stability Factor | [7 empty] | 5.1818 | 4.0909 | 2.0909 | 3.5455
|  |  |  | 1. The connector temperature cannot exceed the control conductor temperature | [7 empty] | 2. The stability factor “Si” shall not exceed 10 for each of the connector temperature measurements recorded at the specified intervals.
Measurement Points | Cycle Number | Ambient (°C) | Control Conductor (°C) | C1: Connector Resistance (Measured); C1: Connector Resistance (Corrected to 20C)
|  |  |  | Micro Ohms (μΩ) |  |  |  | Micro Ohms (μΩ)
|  |  |  | C1 | C2 | C3 | C4 | C1 | C2 | C3 | C4
1 | 25 | 24 | 123 | 386.1 | 391.6 | 400 | 407.4 | 380.6191 | 386.041 | 394.3218 | 401.6167
2 | 50 | 24 | 124 | 386.8 | 392.1 | 400.4 | 408.4 | 381.3091 | 386.5339 | 394.7161 | 402.6025
3 | 75 | 23 | 125 | 387.4 | 392 | 400.5 | 409.2 | 383.2608 | 387.8116 | 396.2208 | 404.8279
4 | 100 | 24 | 128 | 387.6 | 392 | 401.2 | 409.6 | 382.0978 | 386.4353 | 395.5047 | 403.7855
5 | 125 | 22 | 122 | 384 | 389.4 | 398.6 | 406.2 | 381.255 | 386.6164 | 395.7506 | 403.2963
6 | 165 | 22 | 124 | 386.1 | 391.7 | 400.2 | 408.5 | 383.34 | 388.8999 | 397.3392 | 405.5798
7 | 204 | 25 | 124 | 388.6 | 394.4 | 404.7 | 411.9 | 381.7289 | 387.4263 | 397.5442 | 404.6169
8 | 251 | 24 | 124 | 389.9 | 395.8 | 405.9 | 412 | 384.3651 | 390.1814 | 400.138 | 406.1514
9 | 329 | 24 | 128 | 392.1 | 397.5 | 407.3 | 414.5 | 386.5339 | 391.8573 | 401.5181 | 408.6159
10 | 406 | 25 | 125 | 389 | 394.4 | 404.5 | 411.5 | 382.1218 | 387.4263 | 397.3477 | 404.224
11 | 496 | 23 | 127 | 388.3 | 394 | 403.3 | 410.2 | 384.1512 | 389.7903 | 398.9909 | 405.8172
[5 empty] | Average Resistance |  |  | 382.7984 | 388.0927 | 397.2175 | 404.6486
[5 empty] | Min Acceptable Resistance |  |  | 363.6585 | 368.6881 | 377.3566 | 384.4161
[5 empty] | Max Allowable Resistance |  |  | 401.9383 | 407.4973 | 417.0783 | 424.881
3. The resistance of the connectors tested shall not vary by more than 5% from the average of the measured values.
Note on E20: rwestbrook: Red highlighted values are above the control conductor
Note on M20: rwestbrook: Red Highlights Values out of Tolerance
Note on I41: rwestbrook: RED Highlights values out of tolerance
Note on C6: rwestbrook: Type in AL, CU, ACSR
Note on F6: rwestbrook: Type in AL, CU, ACSR

## Graphs
ANSI C119.1
Heat Cycle Temperature and Resistance Graphs
12345

## Constants
Wire Type | Resistance constants | Class | Method | Type
AL | 0.0036 |  | CCT | Mechanical
CU | 0.004 | A | CCST | Compression
ACSR | 0.004
n/a